LyteFyba BMS
Proposed Modbus Protocol

The LyteFyba Battery Management System can communicate with the system controller using Modbus/ASCII over an RS232 port at 9600 bits per second, with a male D9 connector configured as a DTE. No handshaking is required, and appropriate signals are set so that any system expecting hardware handshaking will be satisfied.
The communications port requires either 8 bits, no parity, and 1 stop bit, or 7 bits, space parity, and 1 stop bit.

Results are read with function code 3 (read holding registers) only. All results are single register. The device address is 247. However, if it is necessary to address the individual Cell Management Units (CMUs), their device addresses will be their cell number (e.g. 1-16 in a typical 48 V LiFePO4 battery).

Parameter name	Register	Type	Units	Range	Equivalent plain-text command
Battery Energy Capacity	43649	Uint16	Wh	0-65,535 Wh	E@
Battery Power Capability	43393	Uint16	W	0-65,535 W	D@
Battery Voltage	40119	Uint16	0.1 V	0-400 V	v
Battery Current	40109	Sint16	0.5 A	-750 to 750 A	l
State Of Charge	40103	Sint16	0.10%	0-100%	f
Maximum Cell Stress	40113	Bit fields		See below	p

Uint16 = unsigned integer, 16 bits, range 0 to 65535
Sint16 = signed integer, 16 bits, range -32768 to 32767

Stress:

      15-7 6 5 4 3 2 1 0
+---------------+---------+---------+---------+---------+---------+---------+---------+
| Always | Comms | Stress type | Stress level (0 to 15 in binary) |
| 0 | error | | |
+---------------+---------+---------+---------+---------+---------+---------+---------+
        Treat 00 don't ignore 0-7 Normal
        as 01 ignore on discharge 8-11 Warning
        stress 10 ignore on charge 12-15 Alarm
        8 11 all in bypass, and (BMU disconnects battery at 15)
        ignore on discharge

Cell stress

The simplest battery monitoring systems use a single alarm-wire which is daisy-chained through all of the CMUs (Cell Management Units) so that if any cell goes outside its safe operating area the circuit is broken. This single-bit all-or-nothing approach does not give the rest of the system any warning of impending disconnection and so the LyteFyba system instead uses a four-bit number (0 to 15) to represent the "stress level" of each cell. Stress may be due to under-voltage, over-voltage, under-temperature, over-temperature, excessive charge current or excessive discharge current (whichever is the worst at the time). Stress levels 7 down to 0 are increasingly safe and levels 8 up to 15 are increasingly unsafe.

At regular intervals, the first CMU sends its stress level to the second CMU which, like all the remaining CMUs, either passes it on or substitutes its own stress level if this is greater. So the stress level that arrives at the BMU a few milliseconds later is the stress level of the most stressed cell. The BMU then makes this available as register 40113 to the system controller, or substitutes a stress level based on the current if this is greater. Stress updates can be configured to be as fast as 15 times per second or as slow as one every 1.9 seconds.

If stress is starting to rise when the system controller is discharging the battery, it can anticipate problems by responding to the increasing stress of say 8 to 9 to 10 by reducing the demand on the battery (direct the inverter to transfer less power). By reacting to the lower levels of stress, a potentially unstable situation where the battery voltage oscillates due to the inverter power surging high and low, as could happen with a single alarm condition, is avoided. Similarly, when charging the battery, as the battery approaches higher states of charge, its impedance rises, making it susceptible to surges. By heeding the lower stress levels and smoothly tapering the charge power, instability is again avoided.

The system controller, battery management system and battery form a control system. Ideally, but not required, a proportional / integral (PI) control algorithm would be used to control both discharge power (and hence current), and charge power (and hence current; the batteries only care about current). That is the reason for the wide range of normal stress levels; a PI control algorithm is able to use these stress levels to better anticipate an alarm condition, resulting in better protection of the battery.

When the stress-type field is 00, 01 or 11, the stress should be treated like maximum cell voltage, and when the stress-type field is 00 or 10, the stress should be treated like minimum cell voltage, except in this case higher stress corresponds to lower cell voltage. If the stress is actually due to temperature or current, the same strategy will act to protect the battery, lowering discharge or charge current as needed. In all cases, the goal is to keep the stress below 8.

– Mike Van Emmerik, 30-Sep-2015